## Compressor Pages List
Compressor_Model | Template | Quantity
ARK66FAAMT | 1 EXD-SH2 | 2
ARK66FAAMT | CD-FAN fans-tech | 1
ARK66FAAMT | ENTH-WHEEL | 1
ARK66FAAMT | 2_Supply_Fan | 1

## Feuil1
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Nominal Capacity | Compressor Manufacturer | Control | Refrigerant | Compressor Skid Model Number | Compressor 1 Qty | Compressor 2 Qty | Minimum Capacity | Compressor Model 200V | Compressor Model 400V | Compressor Model 600V | Compressor Qty | Condenser Airflow | Suction Line Dia | Discharge Line Dia | Liquide Line Dia | Cooling Air Condenser Model | HP Air Condenser Model | Cooling Water Condenser Model | HP Ater Condenser Model | Water Evaporator | Condenser Fan Qty
13 | Mitsubishi | VS | R454B | CSV4M13 | 1 | 0 | 3.25 | ARK66FAAMT | ARK66FAEMT | ARK66FAEMT | 1 | 9000 | 1.375 | 1.125 | 0.875 | ASHP18 | ASHP18 |  |  |  | 1
15 | Mitsubishi | VS | R454B | CSV4M15 | 1 | 0 | 3.75 | ARK78FAAMT | ARK78FAEMT | ARK78FAEMT | 1 | 11000 | 1.375 | 1.125 | 0.875 | ASHP18 | ASHP18 |  |  |  | 1
17 | Mitsubishi | VS | R454B | CSV4M17 | 1 | 0 | 4.25 | ARK87FAAMT | ARK87FAEMT | ARK87FAEMT | 1 | 13000 | 1.375 | 1.125 | 0.875 | ASHP18 | ASHP18 |  |  |  | 1
26 | Mitsubishi | VS | R454B | CSV4M26 | 2 | 0 | 6.5 | ARK66FAAMT | ARK66FAEMT | ARK66FAEMT | 2 | 18000 | 1.625 | 1.375 | 1.125 | ASHP26 | ASHP26 | DFX400x130 |  |  | 2
30 | Mitsubishi | VS | R454B | CSV4M30 | 2 | 0 | 7.5 | ARK78FAAMT | ARK78FAEMT | ARK78FAEMT | 2 | 22000 | 1.625 | 1.375 | 1.125 | ASHP26 | ASHP26 | DFX400x130 |  |  | 2
35 | Mitsubishi | VS | R454B | CSV4M35 | 2 | 0 | 8.75 | ARK87FAAMT | ARK87FAEMT | ARK87FAEMT | 2 | 26000 | 1.625 | 1.375 | 1.125 | ASHP35 | ASHP35 | DFX400x130 |  |  | 2
40 | Mitsubishi | VS | R454B | CSV4M40 | 3 | 0 | 10 | ARK66FAAMT | ARK66FAEMT | ARK66FAEMT | 3 | 33000 | 2.125 | 1.625 | 1.375 | ASHP35 | ASHP35 |  |  |  | 3
45 | Mitsubishi | VS | R454B | CSV4M45 | 3 | 0 | 11.25 | ARK78FAAMT | ARK78FAEMT | ARK78FAEMT | 3 | 36000 | 2.125 | 1.625 | 1.375 | ASHP55 | ASHP55 |  |  |  | 3
50 | Mitsubishi | VS | R454B | CSV4M50 | 3 | 0 | 12.5 | ARK87FAAMT | ARK87FAEMT | ARK87FAEMT | 3 | 39000 | 2.125 | 1.625 | 1.375 | ASHP55 | ASHP55 |  |  |  | 3
13 | Copeland | VS | R454B | CSV4C13 | 1 | 0 | 3.25 | YAW0661E-5X9-ECH | YAW0661E-7X9-ECH | YAW0661E-7X9-ECH | 1 | 9000 | 1.375 | 1.125 | 0.875 | ASHP18 | ASHP18 |  |  |  | 1
17 | Copeland | VS | R454B | CSV4C17 | 1 | 0 | 4.25 | YAW0961E-5X9-ECH | YAW0961E-7X9-ECH | YAW0961E-7X9-ECH | 1 | 13000 | 1.375 | 1.125 | 0.875 | ASHP18 | ASHP18 |  |  |  | 1
26 | Copeland | VS | R454B | CSV4C26 | 2 | 0 | 6.5 | YAW0661E-5X9-ECH | YAW0661E-7X9-ECH | YAW0661E-7X9-ECH | 2 | 18000 | 1.625 | 1.375 | 1.125 | ASHP26 | ASHP26 |  |  |  | 2
35 | Copeland | VS | R454B | CSV4C35 | 2 | 0 | 8.75 | YAW0961E-5X9-ECH | YAW0961E-7X9-ECH | YAW0961E-7X9-ECH | 2 | 26000 | 1.625 | 1.375 | 1.125 | ASHP35 | ASHP35 |  |  |  | 2
40 | Copeland | VS | R454B | CSV4C40 | 3 | 0 | 10 | YAW0661E-5X9-ECH | YAW0661E-7X9-ECH | YAW0661E-7X9-ECH | 3 | 33000 | 2.125 | 1.625 | 1.375 | ASHP35 | ASHP35 |  |  |  | 3
50 | Copeland | VS | R454B | CSV4C50 | 3 | 0 | 12.5 | YAW0961E-5X9-ECH | YAW0961E-7X9-ECH | YAW0961E-7X9-ECH | 3 | 39000 | 2.125 | 1.625 | 1.375 | ASHP55 | ASHP55 |  |  |  | 3
Compressor | Nominal Capacity | Power | Power Input | RLA | RLA Conditions |  | Refrigerant | Type | Composition | ASHRAE Safety Class | GWP₁₀₀ | vs. R-410A (GWP 2,088) |  | Manufacturer | Model # | Part # | Flow | Dia In | Dia Out | Max Cap | Min Cap | Notes
ARK52FAAMT | 9.6106 | 208/3/60 | 11077 | 33.6 | 130,65 |  | R744 | Natural | CO₂ | A1 | 1 | -99.95% |  | Copleand | EX4-I21 | 800 615 | Uni-flow | 0.375 | 0.625 | 6.2572 | 0.62572 | Vapor Inject.
ARK52FABMT | 9.6106 | 575/3/60 | 11044 | 20 | 130,65 |  | R290 | Natural | Propane | A3 | 3 | -99.86% |  | Copleand | EX4-U31 | 800 617 | Bi-Flow | 0.625 | 0.625 | 6.2572 | 0.62572
ARK52FABMT | 9.6106 | 480/3/60 | 11044 | 23.9 | 130,65 |  | R1234ze | HFO | Single-component | A2L | 7 | -99.66% |  | Copleand | EX5-U21 | 800 618 | Uni-flow | 0.625 | 0.875 | 19.0559 | 1.9056
ARK66FAAMT | 13.3984 | 208/3/60 | 14125 | 42.46 | 130,65 |  | R454B | HFC/HFO blend | R-32 / R-1234yf | A2L | 466 | -77.68% |  | Copleand | EX5-U31 | 800 619 | Bi-Flow | 0.875 | 0.875 | 19.0559 | 1.9056 | Cond18T 35T
ARK66FAEMT | 13.3984 | 480/3/60 | 13392 | 19.9 | 130,65 |  | R515B | HFO/HFC blend | R-1234ze(E) / R-227ea | A1 | 299 | -85.68% |  | Copleand | EX6-I21 | 800 620 | Uni-flow | 0.875 | 1.125 | 45.7911 | 4.5791
ARK66FAEMT | 13.3984 | 575/3/60 | 13392 | 16.6 | 130,65 |  | R513A | HFC/HFO blend | R-1234yf / R-134a | A1 | 573 | -72.56% |  | Copleand | EX6-I31 | 800 622 | Bi-Flow | 1.125 | 1.125 | 45.7911 | 4.5791 | Cond 55T
ARK78FAAMT | 14.2966 | 208/3/60 | 15935 | 52.5 | 130,65 |  | R32 | HFC | Single-component | A2L | 675 | -67.67% |  | Copleand | EX7-I21 | 800 624 | Uni-flow | 1.125 | 1.375 | 125.4278 | 12.5428
ARK78FAEMT | 14.2966 | 575/3/60 | 16104 | 23.4 | 130,65 | [8 empty] | Copleand | EX7-U31 | 800 626 | Bi-Flow | 1.375 | 1.375 | 125.4278 | 12.5428
ARK78FAEMT | 14.2966 | 480/3/60 | 16104 | 28.05 | 130,65 | [8 empty] | Danfoss | ETS-12C-12 |  | Bi-Flow | 0.5 | 0.5 | 34.7 | 2.566
ARK87FAAMT | 15.9465 | 208/3/60 | 17908 | 53.54 | 130,65 | [8 empty] | Danfoss | ETS-12C-16 |  | Bi-Flow | 0.625 | 0.625 | 36.92 | 1.714
ARK87FAEMT | 15.9465 | 480/3/60 | 17791 | 29.86 | 130,65 | [8 empty] | Danfoss | ETS-12C-22 |  | Bi-Flow | 0.825 | 0.825 | 39.19 | 1.8 | Cond 35T - 55T
ARK87FAEMT | 15.9465 | 575/3/60 | 17791 | 24.9 | 130,65 | [8 empty] | Danfoss | ETS-24C-12 |  | Bi-Flow | 0.5 | 0.5 | 49.49 | 3.72
ARK100FAEMT | 16.4331 | 575/3/60 | 21296 | 29.09 | 130,65 | [8 empty] | Danfoss | ETS-24C-16 |  | Bi-Flow | 0.625 | 0.625 | 52.01 | 4.34
ARK100FAEMT | 16.4331 | 480/3/60 | 21296 | 34.85 | 130,65 | [8 empty] | Danfoss | ETS-24C-22 |  | Bi-Flow | 0.75 | 0.75 | 64.02 | 5.31
YAW0661E-5X9-ECH | 13.4583 | 208/3/60 | 15450 | 43.5 | 130,65
YAW0661E-7X9-ECH | 13 | 480/3/60 | 14800 | 19.1667 | 130,65
YAW0661E-7X9-ECH | 13 | 575/3/60 | 14800 | 16 | 130,65
YAW0961E-5X9-ECH | 18.5833 | 208/3/60 | 22200 | 80.6 | 130,65
YAW0961E-7X9-ECH | 18.6667 | 480/3/60 | 22800 | 38.2375 | 130,65 | [14 empty] | Copeland
YAW0961E-7X9-ECH | 18.6667 | 575/3/60 | 22800 | 31.92 | 130,65 | [8 empty] | Ball Valve
ARK52FAAMT | 9.6106 | 208/3/60 | 10139 | 31.19 | 125,60 | [8 empty] | Size | Name | Danfos | Copeland | Sporlan | CB Supplies | description
ARK52FABMT | 9.6106 | 575/3/60 | 10474 | 19.1 | 125,60 | [8 empty] | 0.625 | Ball Valve 0,625 | 445 | eer | ere | ere | Ball Valve 0,625 Copeland eer
ARK52FABMT | 9.6106 | 480/3/60 | 10474 | 22.9 | 125,60 | [8 empty] | 0.825 | Ball Valve 0,825 | 234 | ere | ere |  | Ball Valve 0,825 Copeland ere |  | Compressor
ARK66FAAMT | 13.3984 | 208/3/60 | 13407 | 40 | 125,60 | [8 empty] | 1.125 | Ball Valve 1,125 |  |  |  |  | Ball Valve 1,125 Copeland |  | VFD
ARK66FAEMT | 13.3984 | 480/3/60 | 12689 | 18.85 | 125,60 | [8 empty] | 1.375 | Ball Valve 1,375 |  |  |  |  | Ball Valve 1,375 Copeland |  | Ball Valve
ARK66FAEMT | 13.3984 | 575/3/60 | 12689 | 15.7 | 125,60 | [8 empty] | 1.625 | Ball Valve 1,625 |  |  |  |  | Ball Valve 1,625 Copeland |  | Check Valve
ARK78FAAMT | 14.2966 | 208/3/60 | 14982 | 47.99 | 125,60 | [8 empty] | 2.125 | Ball Valve 2,125 |  |  |  |  | Ball Valve 2,125 Copeland |  | EEV
ARK78FAEMT | 14.2966 | 575/3/60 | 15250 | 22.18 | 125,60 | [16 empty] | Pressure releif valve
ARK78FAEMT | 14.2966 | 480/3/60 | 15250 | 26.57 | 125,60 | [8 empty] | Check Valve | [7 empty] | Suction accumulator
ARK87FAAMT | 15.9465 | 208/3/60 | 13687 | 48.58 | 125,60 | [8 empty] | Size | Name | Danfos | Copeland | Sporlan | CB Supplies | description |  | Receiver
ARK87FAEMT | 15.9465 | 480/3/60 | 16845 | 28.19 | 125,60 | [8 empty] | 0.625 | Check Valve 0,625 | 445 | eer | ere | ere | Check Valve 0,625 Copeland eer
ARK87FAEMT | 15.9465 | 575/3/60 | 16845 | 23.5 | 125,60 | [8 empty] | 0.825 | Check Valve 0,825 | 234 | ere | ere |  | Check Valve 0,825 Copeland ere
ARK100FAEMT | 16.4331 | 575/3/60 | 20112 | 27.47 | 125,60 | [8 empty] | 1.125 | Check Valve 1,125 |  |  |  |  | Check Valve 1,125 Copeland
ARK100FAEMT | 16.4331 | 480/3/60 | 20112 | 32.91 | 125,60 | [8 empty] | 1.375 | Check Valve 1,375 |  |  |  |  | Check Valve 1,375 Copeland
YAW0661E-5X9-ECH | 13.4583 | 208/3/60 | 14400 | 40.4 | 125,60 | [8 empty] | 1.625 | Check Valve 1,625 |  |  |  |  | Check Valve 1,625 Copeland
YAW0661E-7X9-ECH | 13 | 480/3/60 | 14100 | 18.2083 | 125,60 | [8 empty] | 2.125 | Check Valve 2,125 |  |  |  |  | Check Valve 2,125 Copeland
YAW0661E-7X9-ECH | 13 | 575/3/60 | 14100 | 15.2 | 125,60
YAW0961E-5X9-ECH | 18.5833 | 208/3/60 | 21600 | 74.1 | 125,60
YAW0961E-7X9-ECH | 18.6667 | 480/3/60 | 21400 | 35.1708 | 125,60
YAW0961E-7X9-ECH | 18.6667 | 575/3/60 | 21400 | 29.36 | 125,60
Nominal Capacity | Application Type | Configuration | Evaporator Capacity | Condenser Capacity | Refrigerant | Ent Liquid Temp | SST | SH | Ent Gas Temp | SDT | SC | Coolant | EWT | LWT | Evap Capacity (TR) | Cond Capacity (kW)
18 | Evaporator | Simple | 219 |  | R454B | 100 | 41 | 5 | N/A | N/A | N/A | Water | 54 | 44 | 18.25 | 0
25 | Evaporator | Simple | 294 |  | R454B | 100 | 41 | 5 | N/A | N/A | N/A | Water | 54 | 44 | 24.5 | 0
36 | Evaporator | Simple | 438 |  | R454B | 100 | 41 | 5 | N/A | N/A | N/A | Water | 54 | 44 | 36.5 | 0
55 | Evaporator | Simple | 657 |  | R454B | 100 | 41 | 5 | N/A | N/A | N/A | Water | 54 | 44 | 54.75 | 0
50 | Evaporator | Dual | 588 |  | R454B | 100 | 41 | 5 | N/A | N/A | N/A | Water | 54 | 44 | 49 | 0
72 | Evaporator | Dual | 876 |  | R454B | 100 | 41 | 5 | N/A | N/A | N/A | Water | 54 | 44 | 73 | 0
110 | Evaporator | Dual | 1314 |  | R454B | 100 | 41 | 5 | N/A | N/A | N/A | Water | 54 | 44 | 109.5 | 0
18 | Condenser | Simple | N/A | 280 | R454B | N/A | N/A | N/A | 170 | 110 | 10 | Water | 95 | 105 | N/A | 82.0393
25 | Condenser | Simple | N/A | 378 | R454B | N/A | N/A | N/A | 170 | 110 | 10 | Water | 95 | 105 | N/A | 110.753
36 | Condenser | Simple | N/A | 560 | R454B | N/A | N/A | N/A | 170 | 110 | 10 | Water | 95 | 105 | N/A | 164.0785
55 | Condenser | Simple | N/A | 840 | R454B | N/A | N/A | N/A | 170 | 110 | 10 | Water | 95 | 105 | N/A | 246.1178
50 | Condenser | Dual | N/A | 756 | R454B | N/A | N/A | N/A | 170 | 110 | 10 | Water | 95 | 105 | N/A | 221.506
72 | Condenser | Dual | N/A | 1120 | R454B | N/A | N/A | N/A | 170 | 110 | 10 | Water | 95 | 105 | N/A | 328.157
110 | Condenser | Dual | N/A | 1680 | R454B | N/A | N/A | N/A | 170 | 110 | 10 | Water | 95 | 105 | N/A | 492.2356
18 | Heat Pump | Simple | 219 | 280 | R454B | 100 | 41 | 5 | 170 | 110 | 10 | Water | 95 | 105 | 18.25 | 82.0393
25 | Heat Pump | Simple | 294 | 378 | R454B | 100 | 41 | 5 | 170 | 110 | 10 | Water | 95 | 105 | 24.5 | 110.753
36 | Heat Pump | Simple | 438 | 560 | R454B | 100 | 41 | 5 | 170 | 110 | 10 | Water | 95 | 105 | 36.5 | 164.0785
55 | Heat Pump | Simple | 657 | 840 | R454B | 100 | 41 | 5 | 170 | 110 | 10 | Water | 95 | 105 | 54.75 | 246.1178
50 | Heat Pump | Dual | 588 | 756 | R454B | 100 | 41 | 5 | 170 | 110 | 10 | Water | 95 | 105 | 49 | 221.506
72 | Heat Pump | Dual | 876 | 1120 | R454B | 100 | 41 | 5 | 170 | 110 | 10 | Water | 95 | 105 | 73 | 328.157
110 | Heat Pump | Dual | 1314 | 1680 | R454B | 100 | 41 | 5 | 170 | 110 | 10 | Water | 95 | 105 | 109.5 | 492.2356
AWHP Capacity | # Circuit | # Compressor | Mitsubishi Compressor model | Copeland Compressor model | Air Condenser Model | Air Condenser Qty | Swep Condenser Model # | Swep Evaporator Model # | SWEP HP Model # | Alfa Laval Condenser Model # | Alfa Laval Evaporator Model # | Alfa Laval HP Model # | Danfoss Condenser Model # | Danfoss Evaporator Model # | Danfoss HP Model #
18 | 1 | 1 | ARK87 | YAW0961E | ASHP18 | 2
25 | 1 | 2 | ARK66 | YAW0661E | ASHP26 | 2
36 | 1 | 2 | ARK87 | YAW0961E | ASHP35 | 2 |  | DFX400x130 | DFX400x130
55 | 1 | 3 | ARK87 | YAW0961E | ASHP55 | 2
50 | 2 | 4 | ARK66 | YAW0661E | ASHP26 | 4
72 | 2 | 4 | ARK87 | YAW0961E | ASHP35 | 4 | DB400x186 | DS500x270 | DFX650x166
110 | 2 | 4 | ARK87 | YAW0961E | ASHP55 | 4 | DB500x290 | DFX650x274 | DFX650x274
Nominal Capacity | Circuit Qty | Compressors Qty | Minimum Capacity | Tur Down Ratio | Refrigerant | Compressor Manufacturer | C1 Compressor Skid | C2 Compressor Skid2 | C3 Compressor Skid | C4 Compressor Skid | C5 Compressor Skid | C6 Compressor Skid
13 | 1 | 1 | 3.25 | 4:1 | R454B | Mitsubishi | CSV4M13 | 0 | 0 | 0 | 0 | 0
15 | 1 | 1 | 3.75 | 4:1 | R454B | Mitsubishi | CSV4M15 | 0 | 0 | 0 | 0 | 0
17 | 1 | 1 | 4.25 | 4:1 | R454B | Mitsubishi | CSV4M17 | 0 | 0 | 0 | 0 | 0
25 | 1 | 2 | 6.5 | 4:1 | R454B | Mitsubishi | CSV4M26 | 0 | 0 | 0 | 0 | 0
26 | 2 | 2 | 3.25 | 8:1 | R454B | Mitsubishi | CSV4M13 | CSV4M13 | 0 | 0 | 0 | 0
30 | 1 | 2 | 7.5 | 4:1 | R454B | Mitsubishi | CSV4M30 | 0 | 0 | 0 | 0 | 0
32 | 2 | 2 | 3.75 | 9:1 | R454B | Mitsubishi | CSV4M15 | CSV4M15 | 0 | 0 | 0 | 0
35 | 1 | 2 | 8.75 | 4:1 | R454B | Mitsubishi | CSV4M35 | 0 | 0 | 0 | 0 | 0
36 | 2 | 2 | 4.25 | 9:1 | R454B | Mitsubishi | CSV4M17 | CSV4M17 | 0 | 0 | 0 | 0
40 | 1 | 3 | 10 | 4:1 | R454B | Mitsubishi | CSV4M40 | 0 | 0 | 0 | 0 | 0
45 | 1 | 3 | 11.25 | 4:1 | R454B | Mitsubishi | CSV4M45 | 0 | 0 | 0 | 0 | 0
50 | 1 | 3 | 12.5 | 4:1 | R454B | Mitsubishi | CSV4M50 | 0 | 0 | 0 | 0 | 0
60 | 2 | 4 | 7.5 | 8:1 | R454B | Mitsubishi | CSV4M30 | CSV4M30 | 0 | 0 | 0 | 0
70 | 2 | 4 | 8.75 | 8:1 | R454B | Mitsubishi | CSV4M35 | CSV4M35 | 0 | 0 | 0 | 0
80 | 2 | 5 | 12.5 | 7:1 | R454B | Mitsubishi | CSV4M50 | CSV4M35 | 0 | 0 | 0 | 0
90 | 2 | 6 | 11.25 | 8:1 | R454B | Mitsubishi | CSV4M45 | CSV4M45 | 0 | 0 | 0 | 0
100 | 2 | 6 | 12.5 | 8:1 | R454B | Mitsubishi | CSV4M50 | CSV4M50 | 0 | 0 | 0 | 0
120 | 3 | 7 | 12.5 | 10:1 | R454B | Mitsubishi | CSV4M50 | CSV4M35 | CSV4M35 | 0 | 0 | 0
135 | 3 | 8 | 12.5 | 11:1 | R454B | Mitsubishi | CSV4M50 | CSV4M50 | CSV4M35 | 0 | 0 | 0
150 | 3 | 9 | 12.5 | 12:1 | R454B | Mitsubishi | CSV4M50 | CSV4M50 | CSV4M50 | 0 | 0 | 0
170 | 4 | 10 | 12.5 | 14:1 | R454B | Mitsubishi | CSV4M50 | CSV4M50 | CSV4M35 | CSV4M35 | 0 | 0
185 | 4 | 11 | 12.5 | 15:1 | R454B | Mitsubishi | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M35 | 0 | 0
200 | 4 | 12 | 12.5 | 16:1 | R454B | Mitsubishi | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M50 | 0 | 0
220 | 5 | 13 | 12.5 | 18:1 | R454B | Mitsubishi | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M35 | CSV4M35 | 0
235 | 5 | 14 | 12.5 | 19:1 | R454B | Mitsubishi | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M35 | 0
250 | 5 | 15 | 12.5 | 20:1 | R454B | Mitsubishi | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M50 | 0
265 | 6 | 16 | 12.5 | 22:1 | R454B | Mitsubishi | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M35 | CSV4M35
280 | 6 | 17 | 12.5 | 23:1 | R454B | Mitsubishi | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M35
300 | 6 | 18 | 12.5 | 24:1 | R454B | Mitsubishi | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M50 | CSV4M50
13 | 1 | 1 | 3.25 | 4:1 | R454B | Copeland | CSV4C13 | 0 | 0 | 0 | 0 | 0
17 | 1 | 1 | 4.25 | 4:1 | R454B | Copeland | CSV4C17 | 0 | 0 | 0 | 0 | 0
25 | 1 | 2 | 6.5 | 4:1 | R454B | Copeland | CSV4C26 | 0 | 0 | 0 | 0 | 0
26 | 2 | 2 | 3.25 | 8:1 | R454B | Copeland | CSV4C13 | CSV4C13 | 0 | 0 | 0 | 0
35 | 1 | 2 | 8.75 | 4:1 | R454B | Copeland | CSV4C35 | 0 | 0 | 0 | 0 | 0
36 | 2 | 2 | 4.25 | 9:1 | R454B | Copeland | CSV4C17 | CSV4C17 | 0 | 0 | 0 | 0
40 | 1 | 3 | 10 | 4:1 | R454B | Copeland | CSV4C40 | 0 | 0 | 0 | 0 | 0
50 | 1 | 3 | 12.5 | 4:1 | R454B | Copeland | CSV4C50 | 0 | 0 | 0 | 0 | 0
70 | 2 | 4 | 8.75 | 8:1 | R454B | Copeland | CSV4C35 | CSV4C35 | 0 | 0 | 0 | 0
80 | 2 | 5 | 12.5 | 7:1 | R454B | Copeland | CSV4C50 | CSV4C35 | 0 | 0 | 0 | 0
100 | 2 | 6 | 12.5 | 8:1 | R454B | Copeland | CSV4C50 | CSV4C50 | 0 | 0 | 0 | 0
120 | 3 | 7 | 12.5 | 10:1 | R454B | Copeland | CSV4C50 | CSV4C35 | CSV4C35 | 0 | 0 | 0
135 | 3 | 8 | 12.5 | 11:1 | R454B | Copeland | CSV4C50 | CSV4C50 | CSV4C35 | 0 | 0 | 0
150 | 3 | 9 | 12.5 | 12:1 | R454B | Copeland | CSV4C50 | CSV4C50 | CSV4C50 | 0 | 0 | 0
170 | 4 | 10 | 12.5 | 14:1 | R454B | Copeland | CSV4C50 | CSV4C50 | CSV4C35 | CSV4C35 | 0 | 0
185 | 4 | 11 | 12.5 | 15:1 | R454B | Copeland | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C35 | 0 | 0
200 | 4 | 12 | 12.5 | 16:1 | R454B | Copeland | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C50 | 0 | 0
220 | 5 | 13 | 12.5 | 18:1 | R454B | Copeland | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C35 | CSV4C35 | 0
235 | 5 | 14 | 12.5 | 19:1 | R454B | Copeland | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C35 | 0
250 | 5 | 15 | 12.5 | 20:1 | R454B | Copeland | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C50 | 0
265 | 6 | 16 | 12.5 | 22:1 | R454B | Copeland | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C35 | CSV4C35
280 | 6 | 17 | 12.5 | 23:1 | R454B | Copeland | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C35
300 | 6 | 18 | 12.5 | 24:1 | R454B | Copeland | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C50 | CSV4C50
Compressor | Manufacturer | Nominal Capacity | Power | Power Input | RLA | RLA Conditions | VFD Copeland | VFD Schneider | VFD Mitsubishi
ARK52FAAMT | Mitsubishi | 9.6106 | 208/3/60 | 11077 | 33.4 | 130,65 |  | ATV630D18M3
ARK52FABMT | Mitsubishi | 9.6106 | 575/3/60 | 11044 | 20 | 130,65 |  | ATV630D18S6
ARK52FABMT | Mitsubishi | 9.6106 | 480/3/60 | 11044 | 23.9 | 130,65 |  | ATV630D18N4
ARK66FAAMT | Mitsubishi | 13.3984 | 208/3/60 | 14125 | 42.46 | 130,65 |  | ATV630D18M3
ARK66FAEMT | Mitsubishi | 13.3984 | 480/3/60 | 13392 | 19.9 | 130,65 |  | ATV630D18N4
ARK66FAEMT | Mitsubishi | 13.3984 | 575/3/60 | 13392 | 16.6 | 130,65 |  | ATV630D18S6
ARK78FAAMT | Mitsubishi | 14.2966 | 208/3/60 | 15935 | 52.5 | 130,65 |  | ATV630D22M3
ARK78FAEMT | Mitsubishi | 14.2966 | 575/3/60 | 16104 | 23.4 | 130,65 |  | ATV630D22S6
ARK78FAEMT | Mitsubishi | 14.2966 | 480/3/60 | 16104 | 28.05 | 130,65 |  | ATV630D22N4
ARK87FAAMT | Mitsubishi | 15.9465 | 208/3/60 | 17908 | 53.54 | 130,65 |  | ATV630D22M3
ARK87FAEMT | Mitsubishi | 15.9465 | 480/3/60 | 17791 | 29.86 | 130,65 |  | ATV630D22N4
ARK87FAEMT | Mitsubishi | 15.9465 | 575/3/60 | 17791 | 24.9 | 130,65 |  | ATV630D22S6 | FR-F860-00450
ARK100FAEMT | Mitsubishi | 16.4331 | 575/3/60 | 21296 | 29.09 | 130,65 |  | ATV630D30S6 | FR-F860-00450
ARK100FAEMT | Mitsubishi | 16.4331 | 480/3/60 | 21296 | 34.85 | 130,65 |  | ATV630D30N4
YAW0661E-5X9-ECH | Copeland | 13.4583 | 208/3/60 | 15450 | 43.5 | 130,65 | EVM-322048
YAW0661E-7X9-ECH | Copeland | 13 | 480/3/60 | 14800 | 19.1667 | 130,65 | EVM-344023
YAW0661E-7X9-ECH | Copeland | 13 | 575/3/60 | 14800 | 16 | 130,65 | EVM-355018
YAW0961E-5X9-ECH | Copeland | 18.5833 | 208/3/60 | 22200 | 80.6 | 130,65 | EVM-322048
YAW0961E-7X9-ECH | Copeland | 18.6667 | 480/3/60 | 22800 | 38.2375 | 130,65 | EVM-344031
YAW0961E-7X9-ECH | Copeland | 18.6667 | 575/3/60 | 22800 | 31.92 | 130,65 | EVM-355034
|  | ASHP-CU |  | WSHP-CU |  | AWHP-2P |  | AWHP-4P
CU base INPUT
Description | Label | Signal | IO # S-1000 | IO # C-600 | Type | Comm type | UNIT | RANGE | OPTION
Cooling Enable | Cool_En | ON/OFF | DI101 |  | Binary | Direct | ON/OFF
Reserved |  | ON/OFF | DI102 |  | Binary | Direct | ON/OFF
Condensing Unit Demand | CU_Dem | 0-10V | AI103 |  | Analog | Direct | % | 0-100%
Hot Gas Reheat Demand | HGR_Dem | 0-10V | AI104 |  | Analog | Direct | % | 0-100% | Hot gas reheat
Outdoor Air Temperature | OAT | 10K T2 | AI105 |  | Analog | Direct | °F | -40 - 158°F
Gas sensor | Gas_Sns | ON/OFF | DI106 |  | Binary | Direct | ON/OFF
Supply Fan Pressure Switch | SFan_PSw | ON/OFF | DI107 |  | Binary | Direct | ON/OFF
Reserved |  |  | DI108
CU circuit input w/o modbus
Description | Label | Signal | IO # S-1000 | IO # C-600 | Type | Comm type | UNIT | RANGE | OPTION
Compressor #-A status | Cp_Sts#-A | ON/OFF |  |  | Binary | Direct | ON/OFF
Compressor #-B status | Cp_Sts#-B | ON/OFF |  |  | Binary | Direct | ON/OFF
Compressor #-C status | Cp_Sts#-C | ON/OFF |  |  | Binary | Direct | ON/OFF
Condenser #-A status | Cd_Sts#-A | 0-10V |  |  | Analog | Direct | % | 0-100%
Condenser #-B status | Cd_Sts#-B | 0-10V |  |  | Analog | Direct | % | 0-100%
Condenser #-C status | Cd_Sts#-C | 0-10V |  |  | Analog | Direct | % | 0-100%
Circuit # Low Pressure Switch | LP_Sw# | ON/OFF |  |  | Binary | Direct | ON/OFF
Circuit # High Pressure Switch | HP_Sw# | ON/OFF |  |  | Binary | Direct | ON/OFF
Circuit # Suction pressure | Suc_P# | 4-20mA |  |  | Analog | Direct | PSIG | 0-200 PSIG
Circuit # Discharge Pressure | Dis_P# | 4-20mA |  |  | Analog | Direct | PSIG | 0-500 PSIG |  |  | WSBoiler |  | ASBoiler
Circuit # Liquid Pressure | Liq_P# | 4-20mA |  |  | Analog | Direct | PSIG | 0-500 PSIG
Circuit # Suction Temperature | Suc_T# | PT1000 |  |  | Analog | Direct | °F | -40 - 158°F
Circuit # Discharge Temperature | Dis_T# | PT1000 |  |  | Analog | Direct | °F | -40 - 158°F
Circuit # Liquid Temperature | Liq_T# | PT1000 |  |  | Analog | Direct | °F | -40 - 158°F
Circuit # Low oil level | LOL# | ON/OFF |  |  | Binary | Direct | ON/OFF
CU base OUTPUT
Description | Label | Signal | IO # S-1000 | IO # C-600 | Type | Comm type | UNIT | RANGE | OPTION
Gas Sensor Alarm | Gas_Alm | ON/OFF |  |  | Binary | Direct | ON/OFF
CU CIRCUIT OUTPUT w/o modbus
Description | Label | Signal | IO # S-1000 | IO # C-600 | Type | Comm type | UNIT | RANGE | OPTION
Compressor #-A Enable | Cp_En#-A | ON/OFF | DO101 |  | Binary | Direct | ON/OFF
Compressor #-A Modulation | Cp_Mod#-A | 0-10V | AO102 |  | Analog | Direct | % | 0-100%
Compressor #-B Enable | Cp_En#-B | ON/OFF | DO103 |  | Binary | Direct | ON/OFF
Compressor #-B Modulation | Cp_Mod#-B | 0-10V | AO104 |  | Analog | Direct | % | 0-100%
Compressor #-C Enable | Cp_En#-C | ON/OFF | DO105 |  | Binary | Direct | ON/OFF
Compressor #-C Modulation | Cp_Mod#-C | 0-10V | AO106 |  | Analog | Direct | % | 0-100%
Condenser fan # Enable | Cd-F_En# | ON/OFF | DO201 |  | Binary | Direct | ON/OFF
Condenser fan # Modulation | Cd-F_Mod# | 0-10V | AO202 |  | Analog | Direct | % | 0-100%
Circuit # Cooling Electric Expansion Valve Enable | EEV-C_En1 | ON/OFF | DO203 |  | Binary | Direct | ON/OFF
Reserved |  |  | DO204 |  | Binary | Direct | ON/OFF
Circuit # Electric Expansion Valve Enable Vapor Injection | EEV-VI_En1 | ON/OFF | DO205 |  | Binary | Direct | ON/OFF |  | Vapor injection
Reserved |  |  | DO206 |  | Binary | Direct | ON/OFF
Circuit # Reheat Valve | Rht-Vlv_Mod1 | 0-10V | AO301 |  | Analog | Direct | % | 0-100% | Hot gas reheat
Circuit # Oil Solenoide Valve | Oil_Vlv_En1 | ON/OFF | DO302 |  | Binary | Direct | ON/OFF
Circuit # Crankcase Heater | CCH_En1 | ON/OFF | DO303 |  | Binary | Direct | ON/OFF
Low Ambient Valve #-A | LA_Mod#-A | 0-10V | AO304 |  | Analog | Direct | % | 0-100% | Low-ambient valve
Low Ambient Valve #-B | LA_Mod#-B | 0-10V | AO305 |  | Analog | Direct | % | 0-100% | Low-ambient valve

## Feuil2
1 EXD-SH2
1 EXD-SH2-1-TRANS
1_Condenser_Fan
2_Condenser_Fan
2_Supply_Fan
3_Return_Fan
3_Supply_Fan
AHU_HEAT_COILee
C063
CD-FAN fans-tech
CD-FAN1-C fans-tech
ENTH-WHEEL
GAS SENSOR
Humidifier
IB-G
SUPPLY DAMPERS
VFD-CD
VFD-L
VFD-l MS